Telecommunications Cost Estimate Information Request

Process for Requesting Telecommunications Fiber Service to a New Solar Farm

- For any new Solar site, the Developer should obtain a formal cost estimate from the appropriate local Telecommunications provider.

- Developer to set up initial site visit with local Telecommunications representative. Developer should bring a conceptual site plan/site map with georeferencing (street names should suffice). Conceptual site plan should identify location of solar farm substation and Control House.

- Developer to participate in a site visit. Telecommunications pedestals, if any, should be recorded on site map/site plan.

- Developer to follow up site visit by sending Telecommunications Engineer a copy of the site sketches and notes taken during site visit.

- Telecommunications Engineer to provide Developer with 1 or 2 viable route options for delivering Telecommunications service to the solar farm project boundary. The routes provided by Telecommunications Engineer are based on delivery from the nearest Telecommunications infrastructure to the Control House.  The routes will also include a preliminary cost estimate.

- Developer to review options, if available, and confirm the selected route with Telecommunications Engineer.

- Telecommunications company may develop a more detailed, accurate design.  With a refined design complete, the revised pricing will be provided to the Developer.

- Developer to create a sketch showing the selected route for Telco from the solar farm boundary to the Control House. This sketch will be used with contracting between Developer and Dominion Energy’s Business Development group. This sketch will then become a document that Dominion Energy can provide to the EPCs when the project goes out for bid.		         (See page 4 of this document)

Clarifications to the Scope of Telco Construction & Installation:

- Developer needs to request a 10MB fiber service.

- Telecommunications will cover the full construction of fiber installation up to the pedestal, which is placed at the property boundary. The cost for this activity is part of Telecommunications company estimate to the Developer.

- Within the solar farm boundary, the EPC shall be responsible to construct the conduit run and pull-boxes to Telecommunications standard.

- Telecommunication standard is 1 (qty) 4-inch diameter Schedule 40 conduit, with pull boxes / handholes every 750 ft. The conduit must be dedicated to Telecommunication.

- Within the solar site, Telecommunications company will pull their fiber from their pedestal to the Control House, via the conduit run constructed by the EPC. The cost for pulling this fiber is also part of the Telecommunications company estimate to the Developer.

- An easement, usually fifteen (15) feet wide, shall be dedicated to Telecommunications company over the conduit route containing their fiber. This easement is required within the solar farm boundary. Telecommunications will address easements/rights-of-way outside the solar farm boundary.

Contacting Telecommunications - Prepared by Developer

All solar projects will require delivery of telecommunications to the project operations Control House building, the cost for which must be accounted for in Dominion’s project cost estimate (L2).

Please include the following information in the body of the email request:

- Developer contact information:

- Name: <Development Company Contact >

- Email: <email address>

- Contact number: <phone number>

- List reason for the request:

- Proposed Utility Scale Solar Site Telecommunications

- Relevant project information:

- Project Name - <name>

- County – <name>

- Utility Scale Solar - <system size>

- Approximate location of the renewable energy facility:

- Address - <closest available address or assigned address>

- Solar Site Entrance - <Lat/Long>

- Control Building - <Lat/Long>

- Include KMZ location pins for Google Earth, if possible.

- Any special instructions or information:

- 10 MBs Internet Circuit delivered to the Control House building.

- Include a simple site plan.  (An example is provided after the notes section)

Notes:

- Ideally, the Solar Farm will already have been given a physical e911 street address.  However, this is often not the case.  Therefore, select the closest known street address that is in proximity to the entrance road for the substation and switchyard. If the address is “closest available” state it as such.

- Using Google Earth, place a “PIN” on the desired location and the lat/long of that point will be generated.

- The Telecommunications cost estimates can take four or more weeks to obtain.  The request should be submitted as part of an acceptable preliminary site plan by the developer to Dominion Business Development.

Example site plan uses an existing solar farm for clarification:

Site Entrance

Control House

10 MB cable service by Telecommunications - Option 1

10 MB cable service by Telecommunications - Option 1

USA-Developer, Inc.  Sample Solar Farm

County, VA

USA-Developer, Inc.  Sample Solar Farm

County, VA

##,### LF cable outside property for $000,000.

#,### LF cable inside property for $00,000.

##,### LF cable outside property for $000,000.

#,### LF cable inside property for $00,000.

Telco responsible for all construction within ROW up to boundary

Telco responsible for all construction within ROW up to boundary

ROW STREET A

ROW STREET A

ROW STREET B

ROW STREET B

Telco will deliver line using EPC installed conduit

Telco will deliver line using EPC installed conduit

Telco Service Pedestal

Telco Service Pedestal

EPC to construct dedicated conduit run with pull-boxes for Fiber delivery

EPC to construct dedicated conduit run with pull-boxes for Fiber delivery

Project/Property Boundary

Project/Property Boundary

SUBSTATION

SUBSTATION

CONTROL HOUSE

CONTROL HOUSE

Sample exhibit:  Telco Service to Control House – Prepared by Developer